

**ISLAMIC REPUBLIC OF AFGHANISTAN**

**Ministry of Finance of Afghanistan (MOF)**

ADDENDUM No. 1

To

Bidding Documents

**FOR**

**Contract No. and Title: NPA/MoF/99/G-5510/ICB Procurement and Installation of IT/Electrical Equipment for Customs Data Center**

Client: Ministry of Finance (MOF)

Country: Islamic Republic of Afghanistan

July 13, 2020

**Addendum No. 1**

For

Procurement and Installation of IT/Electrical for Customs Data Center; Ref; **NPA/MOF/99/G-5510/ICB**

As per ITB 8.1, this AddendumNo.1is issued for theProcurement and Installation of IT/Electrical for Customs Data Center,hereunder and shall take precedence over those contained in the Bidding Document.

The following amendments have been made to the Bidding documents:

**Date: 13-July -2020**

| **No** | **BD References in Chronological order** | Existing texts in the BD | **Amended**  |
| --- | --- | --- | --- |
| 1 | **ITB 22.1** | For **Bid submission purposes**only, the Purchaser’s address is: Attention: Safiullah Alokozai, BFS ManagerAddress: Administrative Office of the President, National Procurement Authority Floor/ Room number: Bidding Facilitation Secretariat Deputy Operation & Resources City: KabulCountry: Afghanistan**The deadline for Bid submission is:** Date: **22 July*, 2020***Time: 10:00 AM (Local time)**Note: In case the specified deadline for bid submission is declared holiday for the purchaser, the bids shall be submitted and opened at the specified time on the next working day.**Bidders ***shall not*** have the option of submitting their Bids electronically.The electronic Bidding submission procedures shall be: ***Not Applicable*** | For **Bid submission purposes**only, the Purchaser’s address is: Attention: Safiullah Alokozai, BFS ManagerAddress: Administrative Office of the President, National Procurement Authority Floor/ Room number: Bidding Facilitation Secretariat Deputy Operation & Resources City: KabulCountry: Afghanistan**The deadline for Bid submission is:** Date: **5 August*, 2020***Time: 10:00 AM (Local time)**Note: In case the specified deadline for bid submission is declared holiday for the purchaser, the bids shall be submitted and opened at the specified time on the next working day.**Bidders ***shall not*** have the option of submitting their Bids electronically.The electronic Bidding submission procedures shall be: ***Not Applicable*** |
| 2 | ITB 25.1 | The Bid opening shall take place at: Address: Administrative Office of the President, National Procurement Authority Floor/ Room number: NPA Conference Room City: KabulCountry: AfghanistanDate: **22 July, 2020**Time: 10:00 AM (Local time)The electronic Bid opening procedures shall be: **Not Applicable** | The Bid opening shall take place at: Address: Administrative Office of the President, National Procurement Authority Floor/ Room number: NPA Conference Room City: KabulCountry: AfghanistanDate: **5 August, 2020**Time: 10:00 AM (Local time)The electronic Bid opening procedures shall be: **Not Applicable** |
| 3 | Section VII – Schedule of Requirements. 1.Technical Specifications**3. 42U Racks with KVM Switch for data center (Quantity: 8 Sets)** | 42U Racks with KVM Switch for data center (Quantity: 8 Sets) | 42U Racks with KVM Switch for data center (Quantity: 10 Sets) |
| 4 | Section VII – Schedule of Requirements. 1.Technical Specifications4; 40 KVA UPS FOR DATA CENTER (Quantity; 2 UNITS) | 40 KVA UPS for data center (quantity: 2 units) | 80 KVA UPS for data center (quantity: 2 units) |
| 5 | Section VII – Schedule of Requirements. 1.Technical Specifications4.1.9: 40 KVA UPS FOR DATA CENTER (Quantity; 2 UNITS) | Back up time: 30 Minute backup on full load.The extra battery should in installed in branded racks as per the vendor standards. | 45 Minutes back up on full load |
| 6 | **Section VII – Schedule of Requirements.** **1.Technical Specifications****10.1.0;HVAC for data center (Quantity: 2 Unit)** | Stulz Cyber Air 3 DX with Direct free cooling or equivalent.  | Stulz Cyber Air 3 DX without free air is required. |
| 7 | **Section VII – Schedule of Requirements.** **1. Technical Specifications** **17. Power Cable**  | 500 meter main power cable with 5x120 MM^2 is mentioned in RFB and trenching is not considered?  | It is confirmed that beside 500 meter cable a standard trenching with minimum of 3 handhold and HDPE pipe is required for connecting the Data center to the main substation inside the CTA because The existing channel does not have enough space which can be used. |
| 8 | **Section VII – Schedule of Requirements.** **1. Technical Specifications** **18.1:Power Distrubution panels**  | UPS-DB 1 SET  |  UPS-DB QTY 2set |
| 9 | **Section VII – Schedule of Requirements.** **1.Technical Specifications** 20; **Underground fuel tank (Quantity: 1 Set)** | The Tank in specifications are 5000 liter while in design it is 6000 liters Please explain which one to be considered? | The fuel tank is 6000 liters armored modular.  |
| 10 | Section VII – Schedule of Requirements. 1.Technical Specifications 1.18; General and Technical Check List | Installation of video conference system with room set up. Bidder responsibility to provide all required accessories for Conference room | Installation of video wall system with room set up. Bidder responsibility to provide all required accessories for Conference room |
| 11 | Section VII – Schedule of Requirements.1.Technical Specifications8; RAISED FLOOR IN DC, NOC AND POWER ROOM AS PER REQUIREMENT FOR 120 SQURE AREAS | Ramp for DC is not counted in document, Ramp will require in Power room exit door and at NOC entrance, kindly add in document | Required in DC door |
| 12 | Section VII – Schedule of Requirements. 1.Technical SpecificationsGeneral and Technical Check List 4. Physical infrastructure and Server room Raise floor, Fire prevention and HVAC System. 4.7  | Bidder should Supply, install, commission and maintain 100KVA AVR | Bidder should Supply, install, commission and maintain 200KVA AVR |
| 13 | Section VII – Schedule of Requirements. 1.Technical SpecificationsGeneral and Technical Check List 4. Physical infrastructure and Server room Raise floor, Fire prevention and HVAC System. 4.8 | Bidder must provide all required Power cable for 100KVA AVR | Bidder must provide all required Power cable for 200KVA AVR |
| 14 | Section VII – Schedule of Requirements. 1.Technical SpecificationsGeneral and Technical Check List 4. Physical infrastructure and Server room Raise floor, Fire prevention and HVAC System. 4.9 | Bidder must provide all required accessories for Installation for 100KVA AVR | Bidder must provide all required accessories for Installation for 200KVA AVR |

All other terms and conditions remain unchanged.

**Signature; Signature; Signature; Signature;**

**Ghayoor ZAHOOR Israr Seyal Mustafa Wahidi Imranulhaq Haqyar**

**Senior Procurement SpecialistSenior Infrastructure Specialist ASYCUDA Technical Member Head of ICT Net work**

**Initialed by; Approved by;**

**Muhammad Jawad AhmadzaiHafizullah Ahmadi**

**Senior Procurement SpecialistActing Director of Procurement**